## SelectionData
Selection Table
flow rate, Q | [m³/h] | 300
throw, LT | [m] | 2
supply temperature, Ts | [°C] | 16
room temperature, Tr | [°C] | 26
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | WT500S | WT500S | WT500S | WT500S
| Size | 125 | 160 | 200 | 250
| # deflectors | 9 | 12 | 24 | 36
| Plenum | WP500S | WP500S | WP500S | WP500S
| Ø Spigot | 125 | 160 | 200 | 250
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open)
duct air velocity, Vduct | [m/s] | 6.7906 | 4.1447 | 2.6526 | 1.6977
effective air velocity, Veff | [m/s] | 5.5003 | 4.019 | 3.0722 | 1.8287
static pressure, DPs | [Pa] | 110.3811 | 55.72 | 13.5516 | 6.7196
total pressure, DPtot | [Pa] | 138.0486 | 66.0269 | 17.7733 | 8.4488
throw velocity, vT @ LT | [m/s] | 0.44256 | 0.3183 | 0.20992 | 0.18009
critical distance | [m] | 2.9081 | 2.1381 | 1.7668 | 1.0824
air temperature @ LT | [°C] | 25.5611 | 25.6405 | 25.5359 | 25.3613
sound power, Lw | [dB(A)] | >55 | 48.6545 | 29.286 | 21.7847
sound pressure, Lp | [dB(A)] | 50.0843 | 40.6545 | 21.286 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | 58.8517 | 53.9223 | 38.6709 | 32.4693
250 | [Hz] | 59.6775 | 49.8342 | 33.6047 | 27.1675
500 | [Hz] | 55.9955 | 45.1331 | 25.3351 | 18.6242
1000 | [Hz] | 60.1143 | 47.9997 | 19.9429 | 9.2745
2000 | [Hz] | 55.1377 | 39.8966 | 14.1237 | < BGL
4000 | [Hz] | 47.0799 | 30.8105 | < BGL | < BGL
8000 | [Hz] | < BGL | < BGL | < BGL | < BGL
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | WT500S | WT500S | WT500S | WT500S
|  | Size | 125 | 160 | 200 | 250
|  | # deflectors | 9 | 12 | 24 | 36
|  | Plenum | WP500S | WP500S | WP500S | WP500S
|  | Ø Spigot | 125 | 160 | 200 | 250
|  | Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open)
THROW
|  | Ak [m²] | 0.015151 | 0.020735 | 0.027125 | 0.04557
|  | K1 [m] | 1.3716 | 1.0002 | 0.75927 | 0.87113
|  | X0 [m] | -0.098223 | 0.18151 | 0.16986 | 0.11173
PRESSURE LOSS
|  | A | 29.5744 | 35.2517 | 85.2179 | 117.9571
|  | B | 0.49254 | 0.53261 | 0.48286 | 0.49
|  | Aduct [m²] | 0.012272 | 0.020106 | 0.031416 | 0.049087
CRITICAL DISTANCE (function of DT)
| at 4°C | A | 1.0215 | 0.46616 | 1.3038 | 1.111
|  | B | -1.7799 | -0.61437 | -2.6196 | -2.6021
| at 6°C | A | 1.0215 | 0.46616 | 1.3038 | 1.111
|  | B | -1.9069 | -0.70744 | -2.7802 | -2.6532
| at 8°C | A | 1.0215 | 0.46616 | 1.3038 | 1.111
|  | B | -1.997 | -0.77347 | -2.8942 | -2.6895
| at 10°C | A | 1.0215 | 0.46616 | 1.3038 | 1.111
|  | B | -2.0669 | -0.82469 | -2.9826 | -2.7176
| at 12°C | A | 1.0215 | 0.46616 | 1.3038 | 1.111
|  | B | -2.124 | -0.86654 | -3.0548 | -2.7406
TEMPERATURE
|  | Ak [m²] | 0.015151 | 0.020735 | 0.027125 | 0.04557
|  | K2 [-] | 0.71321 | 0.48055 | 0.53951 | 0.55089
|  | X0 [m] | 0 | 0.074915 | 0.08542 | 0.15866
SOUND POWER, NR
|  | A | 29.4122 | 29.5466 | 33.278 | 32.2042
|  | B | -114.7911 | -123.9292 | -166.1805 | -167.9111
SOUND POWER, dB(A)
|  | A | 30.3668 | 27.7878 | 31.7443 | 31.2591
|  | B | -115.1211 | -109.841 | -151.7766 | -156.5105
SOUND POWER SPECTRUM
| at 125 Hz | A | 24.8382 | 22.3599 | 24.1873 | 26.3129
|  | B | -82.8199 | -73.6136 | -99.2882 | -117.614
| at 250 Hz | A | 25.8927 | 23.1362 | 27.2856 | 25.5464
|  | B | -88.0088 | -82.1297 | -122.0263 | -118.5439
| at 500 Hz | A | 32.8173 | 27.9588 | 35.2885 | 33.5677
|  | B | -131.1871 | -114.3378 | -175.9431 | -172.8385
| at 1 kHz | A | 42.5499 | 39.875 | 43.9342 | 42.5591
|  | B | -182.5814 | -179.4383 | -230.6484 | -233.4734
| at 2 kHz | A | 50.4033 | 44.676 | 34.843 | 52.8826
|  | B | -232.3517 | -214.9255 | -184.6129 | -307.9223
| at 4 kHz | A | 55.2254 | 49.9984 | 50.5322 | 55.8609
|  | B | -267.9135 | -254.3692 | -289.8567 | -338.1181
| at 8 kHz | A
B
END

## IntermediateCalcul (hidden)
Critical distance
Type | WT500S | WT500S | WT500S | WT500S | #REF!
Size | 125 | 160 | 200 | 250 | #REF!
Plenum | WP500S | WP500S | WP500S | WP500S | #REF!
# deflectors | 9 | 12 | 24 | 36 | #REF!
Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open) | #REF!
A
dT
4 | 1.0215 | 0.46616 | 1.3038 | 1.111 | #REF!
6 | 1.0215 | 0.46616 | 1.3038 | 1.111 | #REF!
8 | 1.0215 | 0.46616 | 1.3038 | 1.111 | #REF!
10 | 1.0215 | 0.46616 | 1.3038 | 1.111 | #REF!
12 | 1.0215 | 0.46616 | 1.3038 | 1.111 | #REF!
B
4 | -1.7799 | -0.61437 | -2.6196 | -2.6021 | #REF!
6 | -1.9069 | -0.70744 | -2.7802 | -2.6532 | #REF!
8 | -1.997 | -0.77347 | -2.8942 | -2.6895 | #REF!
10 | -2.0669 | -0.82469 | -2.9826 | -2.7176 | #REF!
12 | -2.124 | -0.86654 | -3.0548 | -2.7406 | #REF!
dT requested
10
dT1 | 10 | 10 | 10 | 10 | #REF!
dT2 | 12 | 12 | 12 | 12 | #REF!
A1 | 1.0215 | 0.46616 | 1.3038 | 1.111 | #REF!
A2 | 1.0215 | 0.46616 | 1.3038 | 1.111 | #REF!
B1 | -2.0669 | -0.82469 | -2.9826 | -2.7176 | #REF!
B2 | -2.124 | -0.86654 | -3.0548 | -2.7406 | #REF!