## SelectionData
WGC
flow rate, Q | [m³/h] | 150
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | WGC | WGC
| Size ØN [mm] | 125 | 125
| Damper position | / | /
| Plastic side plenum | / | /
|  | Supply | Exhaust
static pressure, DPs | [Pa] | 128.3181 | 112.649
total pressure, DPtot | [Pa] | 135.235 | 119.5658
sound power, Lw | [dB(A)] | 39.3945 | 40.2571
sound pressure, Lp | [dB(A)] | 31.3945 | 32.2571
Sound Spectrum
|  | Lw [dB] | Lw [dB]
125 | [Hz] | < BGL | 40.181
250 | [Hz] | 30.9503 | 34.7894
500 | [Hz] | 33.3057 | 32.0246
1000 | [Hz] | 34.0762 | 33.4782
2000 | [Hz] | 32.9739 | 33.0797
4000 | [Hz] | 33.5833 | 34.4266
8000 | [Hz] | 26.4603 | 31.7504
< BGL : Lw below background level

## TechData (hidden)
|  | Type | WGC | WGC
|  | Size ØN [mm] | 125 | 125
|  | Damper position | / | /
|  | Plastic side plenum | / | /
|  | condition 3 | Supply | Exhaust
THROW |  |  | supply | exhaust
Ak [m²]
K1 [m]
X0 [m]
PRESSURE LOSS
|  | A | 16.4514 | 14.7222
|  | B | 0.45529 | 0.49135
|  | Aduct [m²] | 0.012272 | 0.012272
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 42.1495 | 26.1141
|  | B | -173.4884 | -91.3101
SOUND POWER, dB(A)
|  | A | 36.3134 | 24.2585
|  | B | -142.5585 | -81.2936
SOUND POWER SPECTRUM
| at 125 Hz | A |  | 19.2558
|  | B |  | -56.3029
| at 250 Hz | A | 18.9515 | 16.1686
|  | B | -64.0086 | -46.2258
| at 500 Hz | A | 26.3745 | 22.2049
|  | B | -98.8475 | -79.2361
| at 1 kHz | A | 33.7888 | 24.8981
|  | B | -135.2272 | -91.2772
| at 2 kHz | A | 46.2466 | 24.1881
|  | B | -198.7508 | -88.1178
| at 4 kHz | A | 56.2078 | 26.767
|  | B | -248.0535 | -99.6929
| at 8 kHz | A | 61.6129 | 33.9699
|  | B | -282.2597 | -138.4604
END

## IntermediateCalcul (hidden)
Critical distance
Type | WGC | WGC | #REF! | #REF! | #REF! | #REF!
Size ØN [mm] | 125 | 125 | #REF! | #REF! | #REF! | #REF!
Damper position | / | / | #REF! | #REF! | #REF! | #REF!
Plastic side plenum | / | / | #REF! | #REF! | #REF! | #REF!
condition 3 | Supply | Exhaust | #REF! | #REF! | #REF! | #REF!
A
dT
4 |  |  | #REF! | #REF! | #REF! | #REF!
6 |  |  | #REF! | #REF! | #REF! | #REF!
8 |  |  | #REF! | #REF! | #REF! | #REF!
10 |  |  | #REF! | #REF! | #REF! | #REF!
12 |  |  | #REF! | #REF! | #REF! | #REF!
B
4 |  |  | #REF! | #REF! | #REF! | #REF!
6 |  |  | #REF! | #REF! | #REF! | #REF!
8 |  |  | #REF! | #REF! | #REF! | #REF!
10 |  |  | #REF! | #REF! | #REF! | #REF!
12 |  |  | #REF! | #REF! | #REF! | #REF!
dT requested
#REF!
dT1 |  |  | #REF! | #REF! | #REF! | #REF!
dT2 |  |  | #REF! | #REF! | #REF! | #REF!
A1 |  |  | #REF! | #REF! | #REF! | #REF!
A2 |  |  | #REF! | #REF! | #REF! | #REF!
B1 |  |  | #REF! | #REF! | #REF! | #REF!
B2 |  |  | #REF! | #REF! | #REF! | #REF!

## units (hidden)
dB(A)
NR