## SelectionData
Selection Table SLS / SLB / SLF
flow rate, Q | [m³/h] | 500
diffuser length, L | [mm] | 2000
throw, LT | [m] | 4
supply temperature, Ts | [°C] | 18
room temperature, Tr | [°C] | 26
room attenuation | [NR] | 8
acoustics unit |  | NR
| Type | SL--1 | SL--2 | SL--3 | SL--4 | SL--5 | SL--6 | SL--1 | SL--2 | SL--3 | SL--4 | SL--5 | SL--6
| L [mm] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Airflow direction
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
| Plenum | SP--1 | SP--2 | SP--3 | SP--4 | SP--5 | SP--6 | SP--1 | SP--2 | SP--3 | SP--4 | SP--5 | SP--6
effective air velocity, Veff | [m/s] | 4.5589 | 2.8292 | 2.0511 | 1.6086 | 1.1147 | 0.92894 | 3.8972 | 3.0835 | 2.5509 | 2.1752 | 1.896 | 1.6803
static pressure, DPs | [Pa] | 39.713 | 8.0179 | 4.3848 | 2.4831 | 1.4076 | 1.0844 | 15.5025 | 6.0067 | 3.2305 | 2.0358 | 1.409 | <1
total pressure, DPtot | [Pa] | 44.5164 | 9.8073 | 5.1178 | 3.2161 | 1.7078 | 1.0855 | 20.3059 | 7.7961 | 3.9634 | 2.7687 | 1.7092 | <1
throw velocity, vT @ LT | [m/s] | 0.40332 | 0.36242 | 0.33327 | 0.31667 | 0.18312 | 0.13369 | 0.46575 | 0.44063 | 0.37816 | 0.29753 | 0.23365 | 0.16706
critical distance | [m] | 10.5327 | 4.9555 | 3.1882 | 2.3315 | 1.7218 | 1.5942 | - | - | - | - | - | -
air temperature @ LT | [°C] | 25.712 | 25.563 | 25.3635 | 25.1416 | - | - | - | - | - | - | - | -
sound power, Lw | [NR] | >50 | 28.2639 | 22 | 15.8654 | <15 | <15 | 41.8812 | 24.0342 | <15 | <15 | <15 | <15
sound pressure, Lp | [NR] | 45.0998 | 20.2639 | <15 | <15 | <15 | <15 | 33.8812 | 16.0342 | <15 | <15 | <15 | <15
Sound Spectrum
|  | SP--1: Lw [dB] | Lw [dB]
125 | [Hz] | 57.9163 | 42.5947 | 40.3589 | 32.8009 | - | - | 37.2563 | 27.7888 | - | - | - | -
250 | [Hz] | 56.9833 | 38.5428 | 32.7173 | 27.0122 | - | - | 41.8112 | 31.2626 | - | - | - | -
500 | [Hz] | 56.6148 | 30.3482 | 22.4914 | 14.9006 | - | - | 42.3818 | 27.521 | - | - | - | -
1000 | [Hz] | 49.7021 | 23.2566 | 14.5531 | 5.0196 | - | - | 41.6686 | 23.5618 | - | - | - | -
2000 | [Hz] | 43.0667 | 10.2922 | 0.36934 | < BGL | - | - | 37.3196 | 15.2383 | - | - | - | -
4000 | [Hz] | 34.4526 | 1.3003 | < BGL | < BGL | - | - | 27.1511 | 7.0828 | - | - | - | -
8000 | [Hz] | 3.6766 | 3.6766 | 3.6766 | 3.6766 | - | - | 3.6766 | < BGL | - | - | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  |  | HORIZONTAL FLOW | [5 empty] | VERTICAL FLOW
|  | Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-5 SLB-5 SLF-6 | SLS-6 SLB-6 SLF-6 | SLS-1 SLB-1 | SLS-2 SLB-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-5 SLB-5 SLF-6 | SLS-6 SLB-6 SLF-6
|  | Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
|  | condition 1 | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors out/out | deflectors out/out | deflectors out/out | deflectors out/out | deflectors in/out | deflectors in/out
|  | condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
|  | condition 3 | SP--1 | SP--2 | SP--3 | SP--4 | SP--5 | SP--6 | SP--1 | SP--2 | SP--3 | SP--4 | SP--5 | SP--6
THROW
|  | Ak [m²] | 0.015233 | 0.024545 | 0.033858 | 0.04317 | 0.062297 | 0.074757 | 0.017819 | 0.022521 | 0.027223 | 0.031925 | 0.036627 | 0.041329
|  | K1 [m] | 2.616 | 2.984 | 3.2228 | 3.4578 | 2.402 | 1.921 | 3.2674 | 3.4751 | 3.2791 | 2.7939 | 2.35 | 1.7848
|  | X0 [m] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE LOSS
|  | A | 39.8239 | 88.1777 | 118.3174 | 159.1897 | 215.3756 | 239.8535 | 55.4517 | 93.3568 | 131.2619 | 169.167 | 207.072 | 305.1069
|  | B | 0.49896 | 0.50061 | 0.5061 | 0.49627 | 0.43602 | 0.51153 | 0.54942 | 0.54942 | 0.54942 | 0.54942 | 0.54942 | 0.4942
|  | Aduct [m²] | 0.012272 | 0.020106 | 0.031416 | 0.031416 | 0.049087 | 0.7854 | 0.012272 | 0.020106 | 0.031416 | 0.031416 | 0.049087 | 0.7854
CRITICAL DISTANCE (function of DT)
| at 4°C | A | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
|  | B | -2.1599 | -2.4874 | -2.6789 | -2.8148 | -0.7695 | -0.80294
| at 6°C | A | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
|  | B | -2.2672 | -2.5946 | -2.7862 | -2.9221 | -0.87686 | -0.9103
| at 8°C | A | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
|  | B | -2.3433 | -2.6707 | -2.8623 | -2.9982 | -0.95303 | -0.98647
| at 10°C | A | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
|  | B | -2.4023 | -2.7298 | -2.9213 | -3.0572 | -1.0121 | -1.0456
| at 12°C | A | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
|  | B | -2.4505 | -2.778 | -2.9695 | -3.1054 | -1.0604 | -1.0938
TEMPERATURE
|  | Ak [m²] | 0.01403 | 0.02181 | 0.02959 | 0.03737
|  | K2 [-] | 1.1368 | 1.517 | 1.8973 | 2.2775
|  | X0 [m] | -0.099822 | -0.10102 | -0.10222 | -0.10341
SOUND POWER, NR
|  | A | 31.5349 | 30.2937 | 31.7033 | 32.6709 | 33.0164 | 29.2247 | 34.3684 | 34.0536 | 33.7984 | 33.9549 | 32.2313 | 31.0266
|  | B | -124.6955 | -142.6781 | -156.725 | -168.2022 | -178.9267 | -164.5064 | -151.5593 | -167.6681 | -179.9843 | -184.6509 | -185.0125 | -183.4258
SOUND POWER, dB(A)
|  | A | 28.8317 | 29.7404 | 28.8954 | 31.031 | 29.7666 | 28.3845 | 32.5585 | 31.3428 | 30.3266 | 30.3333 | 29.2608 | 30.089
|  | B | -107.4515 | -134.2798 | -135.2064 | -154.037 | -153.7922 | -153.2885 | -137.9521 | -147.8471 | -154.3312 | -157.653 | -161.1536 | -171.3025
SOUND POWER SPECTRUM
| at 125 Hz | A | 22.5623 | 21.1999 | 22.3969 | 25.4369 | 24.5098 | 23.5197 | 21.2989 | 21.3206 | 21.2216 | 21.4546 | 21.2262 | 23.9628
|  | B | -70.3371 | -78.1363 | -86.9812 | -111.3244 | -109.6844 | -110.2288 | -84.0216 | -93.6086 | -100.7485 | -103.8922 | -109.3849 | -119.0942
| at 250 Hz | A | 25.9845 | 28.1731 | 29.484 | 30.3839 | 30.7052 | 27.179 | 23.5042 | 23.5337 | 23.4186 | 23.6891 | 23.4291 | 28.7392
|  | B | -90.1659 | -120.6906 | -133.7542 | -144.428 | -154.4018 | -140.991 | -91.6431 | -102.3543 | -110.2534 | -113.8521 | -119.8943 | -157.8224
| at 500 Hz | A | 30.715 | 32.8446 | 32.0228 | 33.6826 | 33.7304 | 32.562 | 27.1037 | 27.1376 | 27.0049 | 27.3168 | 27.017 | 33.3444
|  | B | -116.6534 | -154.6788 | -157.9978 | -174.7532 | -184.8864 | -185.4162 | -110.9466 | -125.9949 | -136.6812 | -141.9503 | -149.786 | -197.7829
| at 1 kHz | A | 37.8021 | 38.8025 | 38.3526 | 41.3305 | 41.0368 | 40.4176 | 34.9936 | 35.0374 | 34.8661 | 35.2688 | 34.8818 | 42.3932
|  | B | -162.6972 | -194.6662 | -200.8858 | -226.862 | -236.8568 | -243.4672 | -155.2238 | -173.5725 | -186.7379 | -193.0926 | -202.8615 | -265.1849
| at 2 kHz | A | 43.2873 | 47.3986 | 46.488 | 44.8024 | 48.3467 | 49.171 | 41.0381 | 41.0895 | 40.8886 | 41.3608 | 40.907 | 49.0414
|  | B | -199.6188 | -255.0938 | -259.9889 | -257.3935 | -293.4754 | -313.2577 | -192.9473 | -215.3124 | -231.2472 | -239.0511 | -250.78 | -320.9319
| at 4 kHz | A | 46.4959 | 44.7859 | 54.4997 | 70.436 | 47.5837 | 54.6074 | 37.4589 | 37.5058 | 37.3224 | 37.7534 | 37.3391 | 51.5043
|  | B | -225.9494 | -249.6598 | -320.6496 | -430.4359 | -298.8011 | -362.3074 | -183.3531 | -203.6804 | -218.1744 | -225.2614 | -235.9393 | -348.8947
| at 8 kHz | A | [7 empty] | 34.2415 | 34.075 | 34.4504 | 34.0745
|  | B | [7 empty] | -201.9507 | -211.3383 | -214.9566 | -222.5937
END

## IntermediateCalcul (hidden)
Critical distance
Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-5 SLB-5 SLF-6 | SLS-6 SLB-6 SLF-6 | SLS-1 SLB-1 | SLS-2 SLB-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-5 SLB-5 SLF-6 | SLS-6 SLB-6 SLF-6
Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
condition 1 | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors out/out | deflectors out/out | deflectors out/out | deflectors out/out | deflectors in/out | deflectors in/out
condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
condition 3 | SP--1 | SP--2 | SP--3 | SP--4 | SP--5 | SP--6 | SP--1 | SP--2 | SP--3 | SP--4 | SP--5 | SP--6
A
dT
4 | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
6 | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
8 | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
10 | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
12 | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
B
4 | -2.1599 | -2.4874 | -2.6789 | -2.8148 | -0.7695 | -0.80294
6 | -2.2672 | -2.5946 | -2.7862 | -2.9221 | -0.87686 | -0.9103
8 | -2.3433 | -2.6707 | -2.8623 | -2.9982 | -0.95303 | -0.98647
10 | -2.4023 | -2.7298 | -2.9213 | -3.0572 | -1.0121 | -1.0456
12 | -2.4505 | -2.778 | -2.9695 | -3.1054 | -1.0604 | -1.0938
dT requested
8
dT1 | 8 | 8 | 8 | 8 | 8 | 8
dT2 | 10 | 10 | 10 | 10 | 10 | 10
A1 | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
A2 | 1.387 | 1.387 | 1.387 | 1.387 | 0.47924 | 0.47924
B1 | -2.3433 | -2.6707 | -2.8623 | -2.9982 | -0.95303 | -0.98647
B2 | -2.4023 | -2.7298 | -2.9213 | -3.0572 | -1.0121 | -1.0456

## CorrectionFactors (hidden)
Noise correction - diffuser length
cNR | 3.6766
Throw correction - diffuser length
cK1 | 1.096